## Analysis V
The volumes are based on the assumption that the data sheets data sheets differentiate between evaporator and condenser depending on the main operating mode (cooling / heating)
Chillers
Model | Nominal power [W] | Volume Eva [m3] | Volume Con [m3] | Type of compressor | Type of heat exchanger | Refrigerant
Carrier 30XW-0254 | 273000 | 0.05 | 0.055 | Double rotor screw compressor | Shell and tube heat exchanger | R134a
Carrier 30XW-0552 | 532000 | 0.07 | 0.076 | Double rotor screw compressor | Shell and tube heat exchanger | R134a
Carrier 30XW-0852 | 839000 | 0.098 | 0.137 | Double rotor screw compressor | Shell and tube heat exchanger | R134a
Carrier 30XW-1052 | 1060000 | 0.182 | 0.193 | Double rotor screw compressor | Shell and tube heat exchanger | R134a
RC manta wp T.27.P1 S | 28000 | 0.0028 | 0.0028 | Scroll compressor | Plate heat exchanger | R410a
RC manta wp T.54.P2 S | 63800 | 0.0039 | 0.0039 | Scroll compressor | Plate heat exchanger | R410a
RC manta wp T.90.P2 S | 106000 | 0.0058 | 0.0058 | Scroll compressor | Plate heat exchanger | R410a
RC manta wp T.150.P2 S | 172000 | 0.0087 | 0.0087 | Scroll compressor | Plate heat exchanger | R410a
RC manta wp T.200.P2 S | 222000 | 0.0207 | 0.0207 | Scroll compressor | Plate heat exchanger | R410a
RC manta wp T.300.P4 D | 339000 | 0.0275 | 0.0275 | Scroll compressor | Plate heat exchanger | R410a
Trane RTWD 070HE | 279000 | 0.0402 | 0.0451 | Screw compressor (single) | Tube bundle falling film evaporator | R134a
Trane RTWD 160SE | 570000 | 0.0694 | 0.0875 | Screw compressor (single) | Tube bundle falling film evaporator | R134a
Trane RTWD 200SE | 771400 | 0.0901 | 0.1111 | Screw compressor (single) | Tube bundle falling film evaporator | R134a
Trane RTWD 270HSE | 970900 | 0.1203 | 0.1333 | Screw compressor (single) | Tube bundle falling film evaporator | R134a
Trane CGWN 205 | 182000 | 0.0156 | 0.019 | Scroll compressor (quadruple) | Plate heat exchanger | R410a
Trane CGWN 210 | 311000 | 0.0392 | 0.043 | Scroll compressor (quadruple) | Plate heat exchanger | R410a
Trane CGWN 215 | 506000 | 0.0452 | 0.052 | Spiral compressor (six-fold) | Plate heat exchanger | R407c
Lennox Hydrolean SWH 025 | 25500 | 0.003 | 0.003 | Scroll compressor | Plate heat exchanger | R410a | 4.4 | 5.1
Lennox Hydrolean SWH 035 | 37600 | 0.004 | 0.004 | Scroll compressor | Plate heat exchanger | R410a | 6.5 | 7.9
Lennox Hydrolean SWH 050 | 50300 | 0.0052 | 0.0052 | Scroll compressor | Plate heat exchanger | R410a | 8.9 | 10.4
Lennox Hydrolean SWH 080 | 81800 | 0.0057 | 0.0057 | Scroll compressor | Plate heat exchanger | R410a | 14 | 17.1
Lennox Hydrolean SWH 135 | 131900 | 0.0128 | 0.0128 | Scroll compressor | Plate heat exchanger | R410a | 22.7 | 26.9
|  | 0.0028 | 0.0028
Heat pumps
Model | Nominal power [W] | Volume Eva [m3] | Volume Con [m3] | Type of compressor | Type of heat exchanger | Refrigerant
Carrier 30XWH-0254 | 317000 | 0.055 | 0.05 | Double rotor screw compressor | Shell and tube heat exchanger | R134a
Carrier 30XWH-0552 | 599000 | 0.076 | 0.07 | Double rotor screw compressor | Shell and tube heat exchanger | R134a
Carrier 30XWH-0852 | 967000 | 0.137 | 0.098 | Double rotor screw compressor | Shell and tube heat exchanger | R134a
Carrier 30XWH-1052 | 1190000 | 0.193 | 0.182 | Double rotor screw compressor | Shell and tube heat exchanger | R134a
RC manta wp T.27.P1 S | 35100 | 0.0028 | 0.0028 | Scroll compressor | Plate heat exchanger | R410a
RC manta wp T.54.P2 S | 80000 | 0.0039 | 0.0039 | Scroll compressor | Plate heat exchanger | R410a
RC manta wp T.90.P2 S | 135000 | 0.0058 | 0.0058 | Scroll compressor | Plate heat exchanger | R410a
RC manta wp T.150.P2 S | 217000 | 0.0087 | 0.0087 | Scroll compressor | Plate heat exchanger | R410a
RC manta wp T.200.P2 S | 279000 | 0.0207 | 0.0207 | Scroll compressor | Plate heat exchanger | R410a
RC manta wp T.300.P4 D | 431000 | 0.0275 | 0.0275 | Scroll compressor | Plate heat exchanger | R410a
Trane RTWD 070HE | 311800 | 0.0451 | 0.0402 | Screw compressor (single) | Tube bundle falling film evaporator | R134a
Trane RTWD 160SE | 672700 | 0.0875 | 0.0694 | Screw compressor (single) | Tube bundle falling film evaporator | R134a
Trane RTWD 200SE | 771400 | 0.1111 | 0.0901 | Screw compressor (single) | Tube bundle falling film evaporator | R134a
Trane RTWD 270HSE | 1139800 | 0.1333 | 0.1203 | Screw compressor (single) | Tube bundle falling film evaporator | R134a
Trane CGWN 205 | 214000 | 0.019 | 0.0156 | Scroll compressor (quadruple) | Plate heat exchanger | R410a
Trane CGWN 210 | 400800 | 0.043 | 0.0392 | Scroll compressor (quadruple) | Plate heat exchanger | R410a
Trane CGWN 215 | 591200 | 0.052 | 0.0452 | Spiral compressor (six-fold) | Plate heat exchanger | R407c
Lennox Hydrolean SWH 025 | 28000 | 0.003 | 0.003 | Scroll compressor | Plate heat exchanger | R410a
Lennox Hydrolean SWH 035 | 41400 | 0.004 | 0.004 | Scroll compressor | Plate heat exchanger | R410a
Lennox Hydrolean SWH 050 | 55500 | 0.0052 | 0.0052 | Scroll compressor | Plate heat exchanger | R410a
Lennox Hydrolean SWH 080 | 91700 | 0.0057 | 0.0057 | Scroll compressor | Plate heat exchanger | R410a
Lennox Hydrolean SWH 135 | 145100 | 0.0128 | 0.0128 | Scroll compressor | Plate heat exchanger | R410a
|  | 0.0028 | 0.0028

## Analysis m_flow_nominal
Chillers | [10 empty] | For the mass flows, it is assumed that the data sheetsdata sheets differentiate between evaporator and condenser depending on the main operating mode (cooling / heating) and if data for the condenser is missing, the mass flow in the evaporator is assumed
Model | Nominal power [W] | mEva_flow_nominal [kg/s] | mCon_flow_nominal [kg/s] | Type of compressor | Type of heat exchanger | Refrigerant | VEva_flow_nominal [L/s] | VCon_flow_nominal [L/s] |  | Density [kg/L]
Carrier 30XW-0254 | 273000 | 12.961 | 12.961 | Double rotor screw compressor | Shell and tube heat exchanger | R134a | 13 | 13 | Water | 0.997
Carrier 30XW-0552 | 532000 | 24.925 | 24.925 | Double rotor screw compressor | Shell and tube heat exchanger | R134a | 25 | 25
Carrier 30XW-0852 | 839000 | 39.88 | 39.88 | Double rotor screw compressor | Shell and tube heat exchanger | R134a | 40 | 40
Carrier 30XW-1052 | 1060000 | 49.85 | 49.85 | Double rotor screw compressor | Shell and tube heat exchanger | R134a | 50 | 50
Carrier 30XW-1352 | 1342000 | 63.808 | 63.808 | Double rotor screw compressor | Shell and tube heat exchanger | R134a | 64 | 64
Carrier 30XW-1702 | 1732000 | 82.751 | 82.751 | Double rotor screw compressor | Shell and tube heat exchanger | R134a | 83 | 83
RC frigo screw wp 410 V2 | 394000 | 18.7491 | 22.8756 | Screw compressor (double) | Shell and tube heat exchanger | R134a | 67.7 | 82.6
RC frigo screw wp 700 V2 | 656000 | 31.2947 | 38.4953 | Screw compressor (double) | Shell and tube heat exchanger | R134a | 113 | 139
RC frigo screw wp 1050 V2 | 973000 | 46.2497 | 57.0506 | Screw compressor (double) | Shell and tube heat exchanger | R134a | 167 | 206
RC frigo screw wp 1310 V2 | 1224000 | 58.1583 | 71.7286 | Screw compressor (double) | Shell and tube heat exchanger | R134a | 210 | 259
RC frigo screw wp 1610 V2 | 1505000 | 71.4517 | 88.3453 | Screw compressor (double) | Shell and tube heat exchanger | R134a | 258 | 319
RC manta wp T.27.P1 S | 28000 | 1.3293 | 1.634 | Scroll compressor | Plate heat exchanger | R410a | 4.8 | 5.9
RC manta wp T.54.P2 S | 63800 | 3.0187 | 3.7664 | Scroll compressor | Plate heat exchanger | R410a | 10.9 | 13.6
RC manta wp T.90.P2 S | 106000 | 5.0404 | 6.3143 | Scroll compressor | Plate heat exchanger | R410a | 18.2 | 22.8
RC manta wp T.150.P2 S | 172000 | 8.1699 | 10.2469 | Scroll compressor | Plate heat exchanger | R410a | 29.5 | 37
RC manta wp T.200.P2 S | 222000 | 10.5516 | 13.1826 | Scroll compressor | Plate heat exchanger | R410a | 38.1 | 47.6
RC manta wp T.300.P4 D | 339000 | 16.1182 | 20.2169 | Scroll compressor | Plate heat exchanger | R410a | 58.2 | 73
Trane RTWD 070HE | 279000 | 11.964 | 12.961 | Screw compressor (single) | Tube bundle falling film evaporator | R134a | 12 | 13
Trane RTWD 160SE | 570000 | 19.94 | 24.925 | Screw compressor (single) | Tube bundle falling film evaporator | R134a | 20 | 25
Trane RTWD 200SE | 771400 | 26.919 | 34.895 | Screw compressor (single) | Tube bundle falling film evaporator | R134a | 27 | 35
Lennox Hydrolean SWH 025 | 25500 | 1.2186 | 1.4124 | Scroll compressor | Plate heat exchanger | R410a | 4.4 | 5.1
Lennox Hydrolean SWH 035 | 37600 | 1.8001 | 2.1879 | Scroll compressor | Plate heat exchanger | R410a | 6.5 | 7.9
Lennox Hydrolean SWH 050 | 50300 | 2.4648 | 2.8802 | Scroll compressor | Plate heat exchanger | R410a | 8.9 | 10.4
Lennox Hydrolean SWH 080 | 81800 | 3.8772 | 4.7358 | Scroll compressor | Plate heat exchanger | R410a | 14 | 17.1
Lennox Hydrolean SWH 135 | 131900 | 6.2866 | 7.4498 | Scroll compressor | Plate heat exchanger | R410a | 22.7 | 26.9
| MIN | 1.2186 | 1.4124
|  | 82.751 | 88.3453
Wärmepumpen
Model | Nominal power [W] | mEva_flow_nominal [kg/s] | mCon_flow_nominal [kg/s] | Type of compressor | Type of heat exchanger | Refrigerant | VEva_flow_nominal [L/s] | VCon_flow_nominal [L/s]
Carrier 30XWH-0254 | 317000 | 14.955 | 14.955 | Double rotor screw compressor | Shell and tube heat exchanger | R134a | 15 | 15
Carrier 30XWH-0552 | 599000 | 28.913 | 28.913 | Double rotor screw compressor | Shell and tube heat exchanger | R134a | 29 | 29
Carrier 30XWH-0852 | 967000 | 45.862 | 45.862 | Double rotor screw compressor | Shell and tube heat exchanger | R134a | 46 | 46
Carrier 30XWH-1052 | 1190000 | 56.829 | 56.829 | Double rotor screw compressor | Shell and tube heat exchanger | R134a | 57 | 57
Carrier 30XWH-1352 | 1481000 | 70.787 | 70.787 | Double rotor screw compressor | Shell and tube heat exchanger | R134a | 71 | 71
Carrier 30XWH-1702 | 1969000 | 94.715 | 94.715 | Double rotor screw compressor | Shell and tube heat exchanger | R134a | 95 | 95
RC frigo screw wp 410 V2 | 477000 | 18.1953 | 18.7491 | Screw compressor (double) | Shell and tube heat exchanger | R134a | 65.7 | 67.7
RC frigo screw wp 700 V2 | 830000 | 31.8486 | 31.2947 | Screw compressor (double) | Shell and tube heat exchanger | R134a | 115 | 113
RC frigo screw wp 1050 V2 | 1257000 | 48.4653 | 46.2497 | Screw compressor (double) | Shell and tube heat exchanger | R134a | 175 | 167
RC frigo screw wp 1310 V2 | 1569000 | 60.3739 | 58.1583 | Screw compressor (double) | Shell and tube heat exchanger | R134a | 218 | 210
RC frigo screw wp 1610 V2 | 1976000 | 76.1597 | 71.4517 | Screw compressor (double) | Shell and tube heat exchanger | R134a | 275 | 258
RC manta wp T.27.P1 S | 35100 | 1.2739 | 1.3293 | Scroll compressor | Plate heat exchanger | R410a | 4.6 | 4.8
RC manta wp T.54.P2 S | 80000 | 2.9079 | 3.0187 | Scroll compressor | Plate heat exchanger | R410a | 10.5 | 10.9
RC manta wp T.90.P2 S | 135000 | 4.8742 | 5.0404 | Scroll compressor | Plate heat exchanger | R410a | 17.6 | 18.2
RC manta wp T.150.P2 S | 217000 | 7.8375 | 8.1699 | Scroll compressor | Plate heat exchanger | R410a | 28.3 | 29.5
RC manta wp T.200.P2 S | 279000 | 10.1916 | 10.5516 | Scroll compressor | Plate heat exchanger | R410a | 36.8 | 38.1
RC manta wp T.300.P4 D | 431000 | 15.592 | 16.1182 | Scroll compressor | Plate heat exchanger | R410a | 56.3 | 58.2
Trane RTWD 070HE | 311800 | 12.961 | 11.964 | Screw compressor (single) | Tube bundle falling film evaporator | R134a | 13 | 12
Trane RTWD 160SE | 672700 | 24.925 | 19.94 | Screw compressor (single) | Tube bundle falling film evaporator | R134a | 25 | 20
Trane RTWD 200SE | 771400 | 34.895 | 26.919 | Screw compressor (single) | Tube bundle falling film evaporator | R134a | 35 | 27
Lennox Hydrolean SWH 025 | 28000 | 1.4124 | 1.2186 | Scroll compressor | Plate heat exchanger | R410a | 5.1 | 4.4
Lennox Hydrolean SWH 035 | 41400 | 2.1879 | 1.8001 | Scroll compressor | Plate heat exchanger | R410a | 7.9 | 6.5
Lennox Hydrolean SWH 050 | 55500 | 2.8802 | 2.4648 | Scroll compressor | Plate heat exchanger | R410a | 10.4 | 8.9
Lennox Hydrolean SWH 080 | 91700 | 4.7358 | 3.8772 | Scroll compressor | Plate heat exchanger | R410a | 17.1 | 14
Lennox Hydrolean SWH 135 | 145100 | 7.4498 | 6.2866 | Scroll compressor | Plate heat exchanger | R410a | 26.9 | 22.7
|  | 1.2739 | 1.2186
|  | 94.715 | 94.715